Driven equipment: Not known

| Motor type code |  | NXR 5010-2 |
| --- | --- | --- |
| Motor product code |  | N50602S-4 |
| Motor type |  | Squirrel cage Motor |
| Type of Ex-protection |  | Div. 2, Class I, Group C&D T3A |
| Mounting designation |  | F-1 |
| Enclosure and cooling |  | TEFC |
| Insulation |  | Class F |
| Standards |  | NEMA* |
| Ambient temperature, max. |  | 40 °C |
| Altitude, max. |  | 3300 ft.a.s.l. |
| Duty type |  | Continuous |
| Temp. rise |  | Class F at SF 1.0 |
| Connection of stator winding |  | Delta |
| Rated output |  | 600 HP |
| Voltage |  | 460 V |
| Frequency |  | 60 Hz |
| Speed |  | 3574 rpm |
| Current |  | 691 Amps |
| Locked rotor Amps |  | 690 % |
| Locked rotor torque |  | 130 % |
| Breakdown torque |  | 390 % |
| No load current |  | 264 Amps |
| Rated torque |  | 882 lb-ft |
| Load characteristics | Load % | Current Amps | Efficiency % | Power Factor |
|  | 100 | 691 | 95.9 | 0.85 |
|  | 75 | 551 | 95.7 | 0.80 |
|  | 50 | 430 | 94.9 | 0.69 |
| Sound pressure level: (sinus supply, no load) |  | 90 dB(A), tol. + 3 dB(A), 3 ft |
| Weight of rotor |  | 613 lb |
| Total weight of Motor |  | 4521 lb |
| Inertia rotor / load |  | Approx. 52 lb-ft² / 443 lb-ft² |
| Maximum stalling time |  | 27.5 s (warm) |
| Starting time |  | 6.3 s (U=100%) |
|  |  | 8.6 s (U=90 %) |
| Number of consec. starts |  | 2 / 1 (cold/hot) |
| Maximum number of starts |  | 1000 / year |
| Additional start after |  | 45 min, motor shutdown |
|  |  | 30 min, running at full load |
|  |  | 15 min, running at no load |
| VSD operation |
| Temp. rise |  | Class F |
| Speed range, variable (quadratic) torque |  | 10:1 |
| Speed range, constant torque |  | 2:1 |

Motor type code: NXR 5010-2

| Rated output | 600 HP | Power Factor | 0.85 |
| --- | --- | --- | --- |
| Voltage | 460 V | Rated torque | 882 lb-ft |
| Frequency | 60 Hz | Locked rotor Amps | 690 % |
| Speed | 3574 rpm | Locked rotor torque | 130 % |
| Current | 691 Amps | Breakdown torque | 390 % |

Motor type code: NXR 5010-2

| Rated output | 600 HP | Power Factor | 0.85 |
| --- | --- | --- | --- |
| Voltage | 460 V | Rated torque | 882 lb-ft |
| Frequency | 60 Hz | Locked rotor Amps | 690 % |
| Speed | 3574 rpm | Locked rotor torque | 130 % |
| Current | 691 Amps | Breakdown torque | 390 % |

Motor type code: NXR 5010-2

| Rated output | 600 HP | Power Factor | 0.85 |
| --- | --- | --- | --- |
| Voltage | 460 V | Rated torque | 882 lb-ft |
| Frequency | 60 Hz | Locked rotor Amps | 690 % |
| Speed | 3574 rpm | Locked rotor torque | 130 % |
| Current | 691 Amps | Breakdown torque | 390 % |

Equivalent circuit between phase and neutral (equivalent star)

| Running |  |  |  |
| --- | --- | --- | --- |
|  | Stator resistance R1 (125 °C) | 0.00192 | Rotor resistance R2' (160 °C) | 0.00304 |
|  | Stator reactance X1 | 0.0324 | Rotor reactance X2' | 0.0259 |
|  | Magnetizing reactance Xm | 0.93 | Iron loss resistance RFe | 0.04 k |
| Starting |  |  |  |
|  | Stator resistance R1 (55 °C) | 0.00153 | Rotor resistance R2' (55 °C) | 0.00747 |
|  | Stator reactance X1 | 0.0311 | Rotor reactance X2' | 0.0133 |
| Ambient condition |  |  |  |
|  | Stator resistance R1 (40 °C) | 0.00153 | Rotor resistance R2' (40 °C) | 0.00570 |